## Modbus
Modbus Address | Read/Write | High/Low Byte | Parameter Name | Setting Range | Default | Adj. During Run | Description
100 | RW |  | Auto Run |  |  |  | Commands the starter to run when in Auto mode.
101 | RW |  | Reset Fault |  |  |  | Resets the fault condition when in Auto mode.
102 | RW |  | Reset kWH |  |  |  | Resets the total accumulated kWh.
103 | RW |  | Reset Run Time |  |  |  | Resets the total accumulate run time of the motor.
104 | RW |  | Reset Password |  |  |  | Resets the password back to a value of 0 and disables it.
105 | RW |  | Reset Settings |  |  |  | Resets all user settings back to factory default values.
106 | W | H | Set Date |  |  |  | Sets the system date. Only the 3 least significant bytes are used. From least to most significant byte: year, day, month (0x00MMDDYY)
107 | W | L
108 | W | H | Set Time |  |  |  | Sets the system time. Only the 3 least significant bytes are used. From least to most significant byte: second, hour, day (0x00DDHHSS)
109 | W | L
200 | R |  | System State |  |  |  | System state | system_state
201 | R |  | HOA Mode |  |  |  | Mode of operation | hoa_mode
202 | R |  | Motor State |  |  |  | Motor state | motor_state
203 | R |  | Fault |  |  |  | Currently tripped fault | fault_current
204 | R |  | Alarm 1 |  |  |  | Currently active alarm condition #1 | alarm_1
205 | R |  | Alarm 2 |  |  |  | " " #2 | alarm_2
206 | R |  | Alarm 3 |  |  |  | " " #3 | alarm_3
207 | R |  | Alarm 4 |  |  |  | " " #4 | alarm_4
208 | R |  | Alarm 5 |  |  |  | " " #5 | alarm_5
209 | R |  | D1 Status |  |  |  | Status of dry input terminal D1 (Auto Run / Low Float)
210 | R |  | D2 Status |  |  |  | Status of dry input terminal D2 (Shutdown / High Float)
211 | R |  | D3 Status |  |  |  | Status of dry input terminal D3 (Hand)
212 | R |  | D4 Status |  |  |  | Status of dry input terminal D4 (Auto)
213 | R |  | D5 Status |  |  |  | Status of dry input terminal D5 (
214 | R |  | V1/V2 Status |  |  |  | Status of wet input terminals V1/V2 | terminal_v1_v2
215 | R |  | V3/V4 Status |  |  |  | Status of wet input terminals V3/V4
216 | R |  | O1 Status |  |  |  | Status of output Relay terminal O1
217 | R |  | O2 Status |  |  |  | Status of output Relay terminal O2
218 | R |  | Limit Sw Status |  |  |  | Status of limit switch input
219 | R | H | Date |  |  |  | Read the system date. Only the 3 least significant bytes are used. From least to most significant byte: year, day, month (0x00MMDDYY)
220 | R | L
221 | R | H | Time |  |  |  | Read the system time. Only the 3 least significant bytes are used. From least to most significant byte: second, hour, day (0x00DDHHSS)
222 | R | L
223 | R | H | Model |  |  |  | Starter model
224 | R | L
225 | R | H | Serial |  |  |  | Serial number
226 | R | L
227 | R |  | Power Loss Count |  |  |  | Total amount of times the system has been power-cycled
228 | R | H | Motor Run Time |  |  |  | Accumulated motor run time | motor_run_time
229 | R | L
230 | R | H | Power-On Time |  |  |  | Accumulated system power-on time
231 | R | L
232 | R | H | I/O Ver |  |  |  | I/O device firmware version. Periods are implied after 2 and 4 decimal digits (10203 is v01.02.03)
233 | R | L
234 | R | H | Meter Ver |  |  |  | Meter device firmware version. Periods are implied after 2 and 4 decimal digits (10203 is v01.02.03)
235 | R | L
236 | R | H | Display Ver |  |  |  | Display device firmware version. Periods are implied after 2 and 4 decimal digits (10203 is v01.02.03)
237 | R | L
238 | R | H | I/O Boot Ver |  |  |  | I/O boot loader version. Periods are implied after 2 and 4 decimal digits (10203 is v01.02.03)
239 | R | L
240 | R | H | Meter Boot Ver |  |  |  | Meter boot loader version. Periods are implied after 2 and 4 decimal digits (10203 is v01.02.03)
241 | R | L
242 | R | H | Bluetooth Ver |  |  |  | Bluetooth module firmware version. Periods are implied after 2 and 4 decimal digits (10203 is v01.02.03)
243 | R | L
244 | R | H | Gate Drive Ver |  |  |  | Gate drive firmware version. Periods are implied after 2 and 4 decimal digits (10203 is v01.02.03)
245 | R | L
300 | R |  | Average Voltage |  |  |  | Average voltage across all phases |  | voltage_average
301 | R |  | A-B Voltage |  |  |  | Phase-to-phase voltage |  | voltage_ab
302 | R |  | B-C Voltage |  |  |  | Phase-to-phase voltage |  | voltage_bc
303 | R |  | C-A Voltage |  |  |  | Phase-to-phase voltage |  | voltage_ca
304 | R |  | L-N Voltage |  |  |  | Line-to-neutral voltage |  | voltage_ln
305 | R |  | Frequency |  |  |  | Line frequency |  | frequency
306 | R |  | Phase Order |  |  |  | Phase order |  | phase_order
307 | R |  | Voltage Unbal |  |  |  | Voltage unbalance percentage |  | voltage_unbalance
308 | R |  | A-B Min Voltage |  |  |  | Minimum phase-to-phase voltage during the last start |  | voltage_ab_min
309 | R |  | B-C Min Voltage |  |  |  | Minimum phase-to-phase voltage during the last start |  | voltage_bc_min
310 | R |  | C-A Min Voltage |  |  |  | Minimum phase-to-phase voltage during the last start |  | voltage_ca_min
311 | R |  | Average Current |  |  |  | Average current among all phases |  | current_average
312 | R |  | Phase A Current |  |  |  | Phase current |  | current_a
313 | R |  | Phase B Current |  |  |  | Phase current |  | current_b
314 | R |  | Phase C Current |  |  |  | Phase current |  | current_c
315 | R |  | Ground Current |  |  |  | Ground current |  | current_ground
316 | R |  | Current Unbal |  |  |  | Current unbalance percentage |  | current_unbalance
317 | R |  | Peak Current |  |  |  | Peak inrush current during the last start |  | current_peak
318 | R |  | kW |  |  |  | Real power |  | power_kw
319 | R |  | kVA |  |  |  | Apparent power |  | power_kva
320 | R |  | kVAR |  |  |  | Reactive power |  | power_kvar
321 | R |  | Average PF |  |  |  | Power factor |  | power_pf_average
322 | R |  | Phase A PF |  |  |  | Phase power factor |  | power_pf_a
323 | R |  | Phase B PF |  |  |  | Phase power factor |  | power_pf_b
324 | R |  | Phase C PF |  |  |  | Phase power factor |  | power_pf_c
325 | R |  | kWH |  |  |  | Accumulated kWh |  | power_kwh
326 | R
327 | R |  | Motor Insulation |  |  |  | Measured insulation resistance |  | motor_insulation
328 | R |  | RTD Temperature |  |  |  | Temperature from RTD |  | motor_temp_rtd
329 | R |  | Subtrol X Temperature |  |  |  | Temperate from Subtrol X |  | motor_temp_subtrolx
400 | RW |  | Application |  |  |  | Motor application - Sets specific parameter presets based on selected application.
401 | RW |  | FLA 1 |  |  |  | FLA/SFA/high-speed FLA
402 | RW |  | FLA 2 |  |  |  | Low-speed FLA
403 | RW |  | OL Trip Class |  |  |  | Overload trip class
404 | RW |  | Service Factor |  |  |  | Motor service factor
405 | RW |  | OL Reset |  |  |  | Overload reset method
406 | RW |  | OL Retry |  |  |  | Overload automatic reset attempts
407 | RW |  | OL Rst Delay |  |  |  | Overload automatic reset delay
408 | RW |  | OL Cooldown Enable |  |  |  | Overload cooldown run prevention enable
409 | RW |  | OL Cooldown Time |  |  |  | Overload cooldown time
410 | RW |  | Lck Rotor Enable |  |  |  | Locked rotor enable
411 | RW |  | Stall Enable |  |  |  | Stall enable
412 | RW |  | Ovr Cur Enable |  |  |  | Over current protection enable
413 | RW |  | Ovr Cur Level |  |  |  | Over current level percentage
414 | RW |  | Ovr Cur Delay |  |  |  | Over current delay to trip fault/alarm
415 | RW |  | Ovr Cur Reset |  |  |  | Over current reset method
416 | RW |  | Ovr Cur Retry |  |  |  | Over current automatic reset attempts
417 | RW |  | Ovr Cur Rst Dly |  |  |  | Over current autmoatic reset delay
418 | RW |  | Unbl Cur Enable |  |  |  | Current unbalance protection enable
419 | RW |  | Unbl Cur Level |  |  |  | Current unbalance level percentage
420 | RW |  | Unbl Cur Delay |  |  |  | Current unbalance delay to trip fault/alarm
421 | RW |  | Unbl Cur Reset |  |  |  | Current unbalance reset method
422 | RW |  | Unbl Cur Retry |  |  |  | Current unbalance automatic reset attempts
423 | RW |  | Unbl Cur Rst Dly |  |  |  | Current unbalance automatic reset delay
424 | RW |  | Grnd Flt Enable |  |  |  | Ground fault protection enable
425 | RW |  | Grnd Flt Level |  |  |  | Ground fault level
426 | RW |  | No Cur Enable |  |  |  | No current protection enable
427 | RW |  | Unexp Cur Enable |  |  |  | Unexpected current protection enable
428 | RW |  | Out Cal Enable |  |  |  | Out of calibration protection enable
429 | RW |  | Max Str Enable |  |  |  | Max start time protection enable
430 | RW | H | Nominal Voltage |  |  |  | Nominal voltage
431 | RW | L
432 | RW |  | Ovr Vlt Enable |  |  |  | Over voltage protection enable
433 | RW |  | Ovr Vlt Level |  |  |  | Over voltage level percentage
434 | RW |  | Ovr Vlt Delay |  |  |  | Over voltage delay time
435 | RW |  | Ovr Vlt Reset |  |  |  | Over voltage reset method
436 | RW |  | Ovr Vlt Retry |  |  |  | Over voltage automatic reset attempts
437 | RW |  | Ovr Vlt Rst Dly |  |  |  | Over voltage automatic reset delay
438 | RW |  | Undr Vlt Enable |  |  |  | Under voltage protection enable
439 | RW |  | Undr Vlt Level |  |  |  | Under voltage level percentage
440 | RW |  | Undr Vlt Delay |  |  |  | Under voltage delay time
441 | RW |  | Undr Vlt Reset |  |  |  | Under voltage reset method
442 | RW |  | Undr Vlt Retry |  |  |  | Under voltage autmoatic reset attempts
443 | RW |  | Undr Vlt Rst Dly |  |  |  | Under voltage autmoatic reset delay
444 | RW |  | Unbl Vlt Enable |  |  |  | Voltage unbalance protection enable
445 | RW |  | Unbl Vlt Level |  |  |  | Voltage unbalance level percentage
446 | RW |  | Unbl Vlt Delay |  |  |  | Voltage unbalance delay time
447 | RW |  | Unbl Flt Reset |  |  |  | Voltage unbalance reset method
448 | RW |  | Unbl Vlt Retry |  |  |  | Voltage unbalance automatic reset attempts
449 | RW |  | Unbl Vlt Rst Dly |  |  |  | Voltage unbalance automatic reset delay
450 | RW |  | Rev Phase Enable |  |  |  | Phase reversal protection enable
451 | RW |  | Phase Order |  |  |  | Correct phase order
452 | RW |  | Undr Pwr Enable |  |  |  | Under power protection enable
453 | RW |  | Undr Pwr Level |  |  |  | Under power level percentage
454 | RW |  | Undr Pwr Delay |  |  |  | Under power delay time
455 | RW |  | Undr Pwr Reset |  |  |  | Under power reset method
456 | RW |  | Undr Pwr Retry |  |  |  | Under power automatic reset attempts
457 | RW |  | Undr Pwr Rst Dly |  |  |  | Under power automatic reset delay
458 | RW |  | Ovr Pwr Enable |  |  |  | Over power protection enable
459 | RW |  | Ovr Pwr Level |  |  |  | Over power level percentage
460 | RW |  | Ovr Pwr Delay |  |  |  | Over power delay time
461 | RW |  | Ovr Pwr Reset |  |  |  | Over power reset method
462 | RW |  | Ovr Pwr Retry |  |  |  | Over power automatic reset attempts
463 | RW |  | Ovr Pwr Rst Dly |  |  |  | Over power automatic reset delay
464 | RW |  | Neg Pwr Enable |  |  |  | Negative power protection enable
465 | RW |  | Insul Chk Enable |  |  |  | Insulation check enable
466 | RW |  | Mtr Flt Resist |  |  |  | Insulation resistance fault level
467 | RW |  | Mtr Alrm Resist |  |  |  | Insulation resistance alarm level
468 | RW |  | Subtrol X Enable |  |  |  | Subtrol X protection enable
469 | RW |  | Subtrol X Fault Temp |  |  |  | Subtrol X temperature to trip fault
470 | RW |  | Subtrol X Alarm Temp |  |  |  | Subtrol X temperature to trip alarm
471 | RW |  | Subtrol X Reset Type |  |  |  | Subtrol X reset method
472 | RW |  | Subtrol X Retries |  |  |  | Subtrol X automatic reset attempts
473 | RW |  | Subtrol X Reset Delay |  |  |  | Subtrol X automatic reset delay
474 | RW |  | Flse Str Enable |  |  |  | False start protection enable
475 | RW |  | Flse Str Reset Type |  |  |  | False start reset method
476 | RW |  | Flse Str Retry |  |  |  | False start automatic reset attempts
477 | RW |  | Flse Str Rst Dly |  |  |  | False start automatic reset delay
478 | RW |  | Cycle Fault Enable |  |  |  | Cycle fault protection enable
479 | RW |  | Ovr Temp Enable |  |  |  | RTD over temperature protection enable
480 | RW |  | Ovr Temp RTD Type |  |  |  | RTD sensor type
481 | RW |  | Ovr Temp Fault |  |  |  | RTD temperature to trip fault
482 | RW |  | Ovr Temp Alarm |  |  |  | RTD temperature to trip alarm
483 | RW |  | Ovr Temp Delay |  |  |  | RTD delay to trip fault/alarm
484 | RW |  | Ovr Temp Reset Type |  |  |  | RTD over temperature reset method
485 | RW |  | Ovr Temp Retry |  |  |  | RTD over temperature automatic reset attempts
486 | RW |  | Ovr Temp Rst Dly |  |  |  | RTD over temperature automatic reset delay
500 | RW |  | CT Ratio |  |  |  | Ratio of installed external CT's
501 | RW |  | CT Wraps |  |  |  | Number of times motor leads are wrapped through metering CT's
502 | RW |  | Voltage Ratio |  |  |  | Ratio of external step-up transformer
503 | RW |  | Contactor |  |  |  | LS brand contactor model
504 | RW |  | SCR Model |  |  |  | SCR model
505 | RW |  | Pilot Devices |  |  |  | Pilot device type
506 | RW |  | Power Fail Return |  |  |  | Return mode after a power failure
507 | RW |  | Shutdown Return |  |  |  | Return mode after Shutdown condition is cleared
508 | RW |  | Soft Start Mode |  |  |  | Soft Start Mode
509 | RW |  | Soft Start Ramp Time |  |  |  | Soft Start Ramp Time
510 | RW |  | Soft Start Voltage Level |  |  |  | Soft Start Voltage Level
511 | RW |  | Soft Start Current Limit |  |  |  | Soft Start Current Limit
512 | RW |  | Smart Ramp Enable |  |  |  | Enables compensation for soft starting unloaded motors
513 | RW |  | Soft Stop Mode |  |  |  | Soft Stop Mode
514 | RW |  | Soft Stop Ramp Time |  |  |  | Soft Stop Ramp Time
515 | RW |  | Soft Stop Voltage Level |  |  |  | Soft Stop Voltage Level
516 | RW |  | Soft Start Inside Delta |  |  |  | Enables soft starting of motors connected with inside delta setup.
517 | RW |  | D1 Type |  |  |  | D1 contact type
518 | RW |  | D1 Function |  |  |  | D1 function
519 | RW |  | D2 Type |  |  |  | D2 contact type
520 | RW |  | D2 Function |  |  |  | D2 function
521 | RW |  | D5 Type |  |  |  | D5 contact type
522 | RW |  | D5 Function |  |  |  | D5 function
523 | RW |  | D1/D2 Function |  |  |  | D1/D2 function
524 | RW |  | Limit Sw Func |  |  |  | Limit switch function
525 | RW |  | Limit Sw Delay |  |  |  | Limit switch delay
526 | RW |  | O1 Function |  |  |  | Output relay O1 function
527 | RW |  | O2 Status Level |  |  |  | Output relay O2 status level threshold
528 | RW |  | Start Delay Enable |  |  |  | Enables start delay (works in Hand and Auto)
529 | RW |  | Start Delay Time |  |  |  | Sets start delay time
530 | RW |  | Stop Delay Enable |  |  |  | Enables stop delay (works in Auto only)
531 | RW |  | Stop Delay Time |  |  |  | Sets stop delay time
532 | RW |  | Min Off Time Enable |  |  |  | Enables minimum off time (works in Hand and Auto)
533 | RW |  | Min Off Time |  |  |  | Sets minimum off time
534 | RW |  | Min Run Time Enable |  |  |  | Enables minimum run time (works in Auto only)
535 | RW |  | Min Run Time |  |  |  | Sets minimum run time
536 | RW |  | 2-Speed Decel Time |  |  |  | Sets 2-speed motor deceleration delay (delays low-speed from running after high-speed)
537 | RW |  | Part-Winding Delay Time |  |  |  | Sets part-winding delay time before transitioning
538 | RW |  | Wye-Delay Delay Time |  |  |  | Sets delay time before switching from wye to delta configuration